2-way Thermostatic Control Valve

Typical applications

Temperature control in various systems such as tanks, district‑heating installations, engines, and gear units.

Temperature limitation – prevents excessively low temperatures, functioning as frost protection.

Temperature limitation – prevents overheating in hot‑water pipelines (anti‑scald protection).

Water‑saving systems – maintains a minimum flow through the cooler for proper operation but shuts down unnecessary flow when the temperature is sufficiently low or high.

Key benefits

No external power source required – simple, low cost installation.

No user setting needed, “fit and forget” and tamper‑resistant.

Small number of parts – simple maintenance and low cost of ownership.

Robust design capable of high vibration and shock applications.

Any mounting position and explosion‑proof.

Key features

Flow rates of 0.3–6.5 m³/h.

Housings in carbon steel, 316 stainless steel and NANO treaded 316 stainless steel for saltwater.

DN15 – DN25 – DN25 
  1/2”  –   3/4”  –   1”

Threaded connection, BSPP or NPT.

Tamper‑proof temperature settings from 18°C – 113°C.

Pressure ratings up to 40 bar.

Two-way thermostatic valve is supplied in two versions:

- Opens with rising temperature

- Opens with falling temperature

Accreditations available

SEP

PED (Group 1 & 2 liquids — ensure material compatibility)

ATEX II 2G Ex h IIC T6...T3 Gb X

Complies with relevant EU directives

Overview

Model C thermostatic valves cover multiple sizes and settings for fluid temperature control. They can be mounted in any position and use the expanding wax principle to actuate element assemblies. Typical uses: anti‑scald hot water systems, radiant heating, electronics/battery cooling, pump temperature relief.

Temperature settings: 18°C–113°C. For durability avoid continuous operation within 14°C of the max continuous rating.

Materials

Housing: Carbon steel, 316 stainless steel and NANO treaded 316 stainless steel for saltwater.

Seals: Buna N/Nitrile; Viton; Neoprene.

Elements: Nickel‑plated/Stainless steel

Leak holes

Optional leak holes 1 – 5 mm to allow small sensing flow.

Applications

Water saving: maintains minimum cooler flow; consider internal leakhole for sensing.

Valve characteristics

Recommended sizing Δp: 0.14–0.5 bar.

Flow rate (m³/hr) – Water

The flow values shown in the table below apply to a fully open valve and water as the medium.

Flow coefficient (calculated)

Kv is the metric flow coefficient used to describe the hydraulic capacity of a valve. It expresses how much water can flow through the valve under standardized conditions. Kv is defined as the volumetric flow of water in cubic meters per hour (m³/h) at a temperature of 16 °C, passing through the valve with a pressure drop of 1 bar. In practical terms, a higher Kv value means a valve allows more flow for a given pressure drop, while a lower Kv indicates a more restrictive valve.

Temperature and element characteristics

Element type and seal material

Specification

Weights (approx.)

3 kg for all sizes in carbon steel, 316 stainless steel and NANO treaded 316 stainless steel.

Maintenance & service parts (highlights)

Recommended service interval: ≤ 36 months.

Standard configurations STOCKED

2-WAY DN15, DN20 and DN25, BSPP, 316SS, STD ELEMENT, NITRILE, MANY DIFFERENT SETTEMP.

Stocked SETTEMP

Set temp 18°C 
Set temp 24°C 
Set temp 29°C 
Set temp 35°C

Set temp 38°C 
Set temp 43°C 
Set temp 49°C

Set temp 54°C 
Set temp 60°C

How to define the model code